{"text_format":"2","workbook":"xlsx","n_sheets":8,"sheets":["Sheet3","22.05","FCU V.V 밀림","선작업(05.09)","22.06","22.06(1)","22.07","22.08"],"not_rendered":{"charts":0,"images":3,"macros":0,"external_links":0,"defined_names":0,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"run_cost":"one","rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900"}

{"sheet":"Sheet3","index":0,"n_rows":34,"n_cols":14,"rows_kept":34,"cut":false,"hidden":true,"merged":[[33,7,44,14],[25,1,26,1],[6,8,6,11],[6,13,6,14],[7,0,7,1],[7,7,7,10],[7,11,7,14],[8,7,19,10],[8,11,19,14],[10,1,17,1],[18,1,22,1],[23,1,24,1],[20,7,20,10],[20,11,20,14],[21,7,32,10],[21,11,32,14]]}
[null,"목 차"]
[]
[]
[]
[]
[]
[{"$nulls":5},"2022년 동계",null,"보수","FCU MOTOR 소음 및 풍량 저하, 코일막힘",null,null,null,"업체","퍼스트산업개발"]
["FCU 사양",null,"SFC-20F (4구)","SFC-30F (5구)","SFC-40F (6구)","SFC-60F(8구)",null,"FCU Motor 교체 (SFC-40F) 6EA",null,null,null,"FCU Motor 교체 (SFC-30F) 8EA"]
[]
["번호","관 별","위 치","문제점","사 양","교체일자"]
[1,"남제관","1441호","풍량","SFC-40F (6구)","2022-01-25"]
[2,null,"1308호","풍량","SFC-40F (6구)","2022-01-25"]
[3,null,"1416호","풍량","SFC-40F (6구)","2022-01-25"]
[4,null,"1339호","풍량","SFC-40F (6구)","2022-01-25"]
[5,null,"1418앞 복도","풍량","SFC-30F(5구)","대체"]
[6,null,"1419호","풍량","SFC-30F(5구)","2022-01-25"]
[7,null,"1337호","풍량","SFC-30F(5구)","2022-01-25"]
[8,null,"1132호","소음","SFC-30F(5구)","2022-01-25"]
[9,"화홍관","4층 자습실(우)","풍량","SFC-30F(5구)","대체"]
[10,null,"5413호","풍량","SFC-30F(5구)","2022-01-25"]
[11,null,"5113호","풍량","SFC-40F (6구)","2022-01-25",null,"FCU 코일교체 (SFC-40F) 1EA"]
[12,null,"5120호","풍량","SFC-30F(5구)","2022-01-25",null,"\n\n\n\n\n",null,null,null,"\n\n\n\n\n"]
[13,null,"5501호","소음","SFC-30F(5구)","2022-01-25"]
[14,"광교관","6227호","코일교체(막힘)","SFC-40F (6구)","2022-01-25"]
[15,null,"6405호","소음","SFC-40F (6구)","2022-01-25"]
["대체","남제관","1135호","풍량","SFC-30F(5구)","2022-01-25"]
["대체",null,"1222호","풍량","SFC-30F(5구)","2022-01-25"]
[{"$nulls":4},"SFC-30F(5구)",8]
[{"$nulls":4},"SFC-40F (6구)",7]
[{"$nulls":4},"합  계",{"$f":"SUM(F28:F29)","v":15}]
[]
[]
[]
[{"$nulls":7},"□ 생활관 FCU Motor 및 코일교체\n\n2. FCU Motor 교체 (SFC-30F) 8EA\n3. FCU Motor 교체 (SFC-40F) 6EA\n4. FCU Coil 교체 (SFC-40F) 1EA\n\n\n\n\n"]

{"sheet":"22.05","index":1,"n_rows":87,"n_cols":6,"rows_kept":87,"cut":false,"hidden":true,"merged":[[5,0,5,1],[8,1,22,1],[47,0,47,1],[79,3,80,3],[81,3,84,3],[60,1,69,1],[50,1,59,1],[23,1,29,1],[30,1,40,1],[41,1,44,1]]}
[]
[]
[]
[]
[{"$nulls":5},"2022년 동계"]
["FCU 사양",null,"SFC-20F (4구)","SFC-30F (5구)","SFC-40F (6구)","SFC-60F(8구)"]
[]
["번호","관 별","위 치","문제점","사 양","교체일자"]
[1,"남제관","1112호","풍량,소음","SFC-40F (6구)","22.05.02"]
[2,null,"1층로비(동남방향)","소음","SFC-60F (8구)","22.05.02"]
[3,null,"1144호","풍량","SFC-40F (6구)","22.05.02"]
[4,null,"1130호","풍량","SFC-30F(5구)","22.05.02"]
[5,null,"1131호","풍량","SFC-30F(5구)","22.05.02"]
[6,null,"1132호","풍량","SFC-30F(5구)","22.05.02"]
[7,null,"1133호","풍량","SFC-30F(5구)","22.05.02"]
[8,null,"1134호","풍량","SFC-30F(5구)","22.05.02"]
[9,null,"1208호","풍량","SFC-40F (6구)","22.05.02"]
[10,null,"1214호","풍량","SFC-40F (6구)","22.05.02"]
[11,null,"1227앞 복도","소음","SFC-30F(5구)","22.05.02"]
[12,null,"1333앞 복도","소음","SFC-30F(5구)","22.05.02"]
[13,null,"1406호앞 복도","소음","SFC-30F(5구)","22.05.02"]
[14,null,"1418호앞 복도","소음","SFC-30F(5구)","22.05.02"]
[15,null,"1437호앞 복도","소음","SFC-30F(5구)","22.05.02"]
[16,"화홍관","4층 자습실(우)","풍량","SFC-20F(4구)","선작업"]
[17,null,"5303호","풍량","SFC-30F(5구)","22.05.02"]
[18,null,"5325호","풍량","SFC-30F(5구)","22.05.02"]
[19,null,"5216호","풍량","SFC-40F (6구)","22.05.02"]
[20,null,"1층휴게실좌측","풍량","SFC-40F (6구)","22.05.02"]
[21,null,"1층중앙 ATM","풍량","SFC-30F(5구)","22.05.02"]
[22,null,"1층중앙 ATM","풍량","SFC-30F(5구)","22.05.02"]
[23,"용지관","2517호","풍량","SFC-40F (6구)","22.05.03"]
[24,null,"2528호","풍량","SFC-40F (6구)","22.05.03"]
[25,null,"동측복도","풍량","SFC-30F(5구)","22.05.03"]
[26,null,"2413호","소음","SFC-40F (6구)","22.05.03"]
[27,null,"2411호","소음","SFC-40F (6구)","22.05.03"]
[28,null,"2420호","풍량","SFC-40F (6구)","22.05.03"]
[29,null,"2325호","소음","SFC-40F (6구)","22.05.03"]
[30,null,"2327호","소음","SFC-40F (6구)","22.05.03"]
[31,null,"2222호","소음","SFC-40F (6구)","22.05.03"]
[32,null,"2123호","소음","SFC-40F (6구)","22.05.03"]
[33,null,"2층 휴게실 우측","소음","SFC-40F (6구)","22.05.03"]
[34,"광교관","6508호","풍량","SFC-40F (6구)","22.05.03"]
[35,null,"6515호","풍량","SFC-40F (6구)","22.05.03"]
[36,null,"6516호","풍량","SFC-40F (6구)","22.05.03"]
[37,null,"6518호","풍량","SFC-40F (6구)","22.05.03"]
[]
[{"$nulls":5},"2022년 동계"]
["FCU 사양",null,"SFC-20F (4구)","SFC-30F (5구)","SFC-40F (6구)","SFC-60F(8구)"]
[]
["번호","관 별","위 치","문제점","사 양","교체일자"]
[38,"광교관",6528,"소음","SFC-40F (6구)","22.05.03"]
[39,null,6310,"풍량","SFC-40F (6구)","22.05.03"]
[40,null,"2층 자습실 좌측","작동불","SFC-20F(4구)","22.05.03"]
[41,null,"6107호","풍량","SFC-40F (6구)","22.05.03"]
[42,null,"1층 (동)휴게실좌측","풍량","SFC-60F (8구)","22.05.03"]
[43,null,"1층 미화반 우측","소음","SFC-20F(4구)","22.05.03"]
[44,null,"6116호","소음","SFC-60F (8구)","22.05.03"]
[45,null,"6112호","소음","SFC-60F (8구)","22.05.03"]
[46,null,"6225호","소음","SFC-40F (6구)","22.05.03"]
[47,null,"6326호","소음","SFC-40F (6구)","22.05.03"]
[48,"국제학사","7324호","누수","Coil교체","22.05.04"]
[49,null,"7425호","누수","Coil교체","22.05.04"]
[50,null,"7505호","누수","Coil교체","22.05.04"]
[51,null,"7726호","누수","Coil교체","22.05.04"]
[52,null,"7412호","누수","Coil교체","22.05.04"]
[53,null,"7817호","누수","Coil교체,드레인펌프","22.05.04"]
[54,null,"7506호","누수","Coil교체","22.05.04"]
[55,null,"7312호","누수","Coil교체","22.05.04"]
[56,null,"7812호","누수","Coil교체","22.05.04"]
[57,null,"7516호","누수","Coil교체","22.05.04"]
[58,"추가","7325호","누수","Coil교체,드레인펌프","22.05.04"]
[59,"추가","7206호","누수","Coil교체","22.05.04"]
{"$rows_empty":7}
[null,null,null,"Spare 구입","SFC-30F(5구)",5]
[{"$nulls":4},"SFC- 40F(6구)",5]
[null,null,null,"남제관,용지관\n화홍관,광교관","SFC-20F(4구)",3]
[{"$nulls":4},"SFC-30F(5구)",15]
[{"$nulls":4},"SFC- 40F(6구)",25]
[{"$nulls":4},"SFC-60F(8구)",4]
[null,null,null,"국제학사 FCU","Coil 교체(2엽) ",10]
[{"$nulls":4},"합  계",{"$f":"SUM(F78:F86)","v":67}]

{"sheet":"FCU V.V 밀림","index":2,"n_rows":30,"n_cols":6,"rows_kept":30,"cut":false,"hidden":true,"merged":[[8,1,13,1],[5,0,5,1]]}
[]
[]
[]
[]
[{"$nulls":5},"2022년 동계"]
["FCU 사양",null,"SFC-20F (4구)","SFC-30F (5구)","SFC-40F (6구)","SFC-60F(8구)"]
[]
["번호","관 별","위 치","문제점","사 양","교체일자"]
[38,"국제학사","7425호","밸브밀림","15A"]
[39,null,"7817호","밸브밀림","15A"]
[40,null,"7312호","밸브밀림","15A"]
[41,null,"7516호","밸브밀림","15A"]
[42,null,"7325호","밸브밀림","15A"]
[43,null,"7206호","밸브밀림","15A"]
[44]
[45]
[46]
[47]
[48]
[49]
[50]
[51]
[52]
[53]
[54]
[55]
[56]
[57]
[58]
[59]

{"sheet":"선작업(05.09)","index":3,"n_rows":23,"n_cols":8,"rows_kept":23,"cut":false,"hidden":true,"merged":[[8,1,16,1],[19,3,22,3],[5,0,5,1]]}
[]
[]
[]
[{"$nulls":6},"정산완료","5/5일 작업충 추가발생으로 정산완료"]
[{"$nulls":5},"2022년 05월"]
["FCU 사양",null,"SFC-20F (4구)","SFC-30F (5구)","SFC-40F (6구)","SFC-60F(8구)"]
[]
["번호","관 별","위 치","문제점","사 양","교체일자"]
[1,"국제학사","7726호","누수","모터교체","2022-05-09"]
[2,null,"7412호","누수","모터교체","2022-05-09"]
[3,null,"7312호","누수","모터교체","2022-05-09"]
[4,null,"7812호","누수","모터교체","2022-05-09"]
[5,null,"7516호","누수","모터교체","2022-05-09"]
[6,null,"7325호","누수","Coil교체","2022-05-09"]
[7,null,"7325호","누수","드레인펌프 교체","2022-05-09"]
[8,null,"7206호","누수","Coil교체","2022-05-09"]
[9,null,"7206호","누수","모터교체","2022-05-09"]
[]
[]
[null,null,null,"국제학사 FCU","Coil 교체(2엽) ",2]
[{"$nulls":4},"모터교체",6]
[{"$nulls":4},"드레인펌프 교체",1]
[{"$nulls":4},"합   계",{"$f":"SUM(F20:F22)","v":9}]

{"sheet":"22.06","index":4,"n_rows":23,"n_cols":7,"rows_kept":23,"cut":false,"hidden":true,"merged":[[5,0,5,1],[8,1,16,1],[19,3,22,3],[10,2,11,2]]}
[]
[]
[]
[{"$nulls":6},"의뢰완료"]
[{"$nulls":5},"2022년 06월"]
["FCU 사양",null,"SFC-20F (4구)","SFC-30F (5구)","SFC-40F (6구)","SFC-60F(8구)"]
[]
["번호","관 별","위 치","문제점","사 양","교체일자"]
[1,"국제학사","7626호","누수","드레인펌프 교체","2022-05-13"]
[2,null,"7823호","누수","드레인펌프 교체","2022-05-16"]
[3,null,"7313호","누수","드레인펌프 교체","2022-05-16"]
[4,null,null,"전원","PCB 기판교체","2022-05-16"]
[5]
[6]
[7]
[8]
[9]
[]
[]
[null,null,null,"국제학사 FCU"]
[{"$nulls":4},"PCB기판 교체",1]
[{"$nulls":4},"드레인펌프 교체",3]
[{"$nulls":4},"합   계",{"$f":"SUM(F20:F22)","v":4}]

{"sheet":"22.06(1)","index":5,"n_rows":23,"n_cols":6,"rows_kept":23,"cut":false,"hidden":true,"merged":[[5,0,5,1],[19,3,22,3]]}
[]
[]
[]
[]
[{"$nulls":5},"2022년 06월"]
["FCU 사양",null,"SFC-20F (4구)","SFC-30F (5구)","SFC-40F (6구)","SFC-60F(8구)"]
[]
["번호","관 별","위 치","문제점","사 양","교체일자"]
[1,"국제학사","7205호","누수","드레인펌프 교체","2022-06-24"]
[2,"국제학사","6층 휴게실","누수","드레인펌프 교체","2022-06-24"]
[3,"국제학사","8층 서측 탈의실","누수","드레인펌프교체","2022-06-24"]
[4,"광교관","3층자습실","모터불량","SFC-20F","2022-06-24"]
[5,"국제학사","5층 동 탈의실","전원","PCB 기판교체/펌프","2022-06-29"]
[6,"국제학사","5층 동 탈의실","누수","드레인펌프 교체","2022-06-29"]
[7,"국제학사","7305호","누수","드레인펌프 교체","2022-06-29"]
[8,"국제학사","7412호","누수","드레인펌프 교체","2022-06-29"]
[9,"국제학사","7313호","누수","드레인펌프 교체","2022-06-17"]
[10,"국제학사","7823호","누수","드레인펌프 교체","2022-06-17"]
[]
[null,null,null,"국제학사 FCU","SFC-20F",1]
[{"$nulls":4},"PCB기판 교체",1]
[{"$nulls":4},"드레인펌프 교체",8]
[{"$nulls":4},"합   계",{"$f":"SUM(F20:F22)","v":10}]

{"sheet":"22.07","index":6,"n_rows":29,"n_cols":8,"rows_kept":29,"cut":false,"hidden":true,"merged":[[5,0,5,1],[19,3,22,3]]}
[]
[]
[]
[]
[{"$nulls":5},"2022년 07월",null,"견적서 의뢰요함"]
["FCU 사양",null,"SFC-20F (4구)","SFC-30F (5구)","SFC-40F (6구)","SFC-60F(8구)",null,"8월 의뢰 완료"]
[]
["번호","관 별","위 치","문제점","사 양","교체일자"]
[1,"국제학사","7812호","누수","PCB 기판 교체","2022-07-13"]
[2,"국제학사","7812호","누수","드레인펌프 교체","2022-07-13"]
[3,"국제학사","8층 서측샤워실","전원 미공급","PCB 기판 교체","2022-07-13"]
[4,"국제학사","7624호","누수","드레인판 교체","사이즈불량"]
{"$rows_empty":7}
[null,null,null,"국제학사 FCU"]
[{"$nulls":4},"PCB기판 교체",1]
[{"$nulls":4},"드레인펌프 교체",2]
[{"$nulls":4},"합   계",{"$f":"SUM(F20:F22)","v":3}]
[]
[]
[]
[]
[]
[null,"국제학사","7808호","누수","드레인펌프 교체","양호"]

{"sheet":"22.08","index":7,"n_rows":45,"n_cols":7,"rows_kept":45,"cut":false,"hidden":false,"merged":[[29,1,32,1],[5,0,5,1],[8,1,12,1],[13,1,16,1],[17,1,23,1],[24,1,28,1]]}
[]
[]
[]
[]
[{"$nulls":5},"2022년 08월"]
["FCU 사양",null,"SFC-20F (4구)","SFC-30F (5구)","SFC-40F (6구)","SFC-60F(8구)"]
[]
["번호","관 별","위 치","문제점","사 양","교체일자"]
[1,"남제관","1435호","소음,풍량","SFC-30F","5구"]
[2,null,"3층(동)독서실앞","풍량","SFC-30F","5구"]
[3,null,"1238호앞 복도","풍량","SFC-30F","5구"]
[4,null,"1211호","소음","SFC-40F","6구"]
[5,null,"1201호","풍량","SFC-40F","6구"]
[6,"용지관","2107호","풍량","SFC-40F","6구"]
[7,null,"2112호","풍량","SFC-40F","6구"]
[8,null,"2117호","풍량","SFC-40F","6구"]
[9,null,"2506호","풍량","SFC-40F","6구"]
[10,"화홍관","1층 ATM기","모터불량","SFC-30F","5구"]
[11,null,"5102호","풍량","SFC-30F","5구"]
[12,null,"5202호","풍량","SFC-30F","5구"]
[13,null,"5301호","풍량","SFC-30F","5구"]
[14,null,"5329호","소음","SFC-40F","6구"]
[15,null,"4층 자습실 2번","풍량","SFC-20F","4구"]
[16,null,"5521호","풍량","SFC-40F","6구"]
[17,"광교관","3층 자습실 1번","풍량","SFC-20F","4구"]
[18,null,"지하독서실우측1","소음","SFC-40F","6구"]
[19,null,"지하독서실우측2","소음","SFC-40F","6구"]
[20,null,"6226호","소음","SFC-40F","6구"]
[21,null,"6529호","소음","SFC-40F","6구"]
[22,"국제학사","7516호","전원 미공급","PCB 기판 교체"]
[23,null,"7812호","전원 미공급","PCB 기판 교체"]
[24,null,"7812호","누수","드레인펌프 교체"]
[25,null,"7625호","소음","모터교체",null,"추가"]
[]
[]
[]
[]
[]
[]
[{"$nulls":4},"드레인펌프",1]
[{"$nulls":4},"PCB 기판",2]
[{"$nulls":4},"SFC-20F",2]
[{"$nulls":4},"SFC-30F",7]
[{"$nulls":4},"SFC-40F",12]
[{"$nulls":4},"합   계",{"$f":"SUM(F40:F44)","v":24}]